Subscribe to DeepL Pro to edit this document.
Visit www.DeepL.com/Pro for more information.

Category B PlusEnergieBautenPlusEnergieBau® Solar Prize

TheRomanCatholic Church of St. Franziskus Ebmatingen  ,built  1989,isemission-free after the 2018/19  energy-saving  renovation. Thanks to considerably improved roof insulation, the solar-powered geothermal heat pump ,   solar heat utilisationwith 161 m2 of photovoltaic-thermal modules (PVT) and   LED lighting, the previous total energy requirement of 84,400 kWh/a hasbeen reduced by around 35% to 54,700 kWh/a. The old  oil heatingsystemwas  torn out. This saved  7,000 litres of heating oil  per yearand avoided  21 t CO2 emissions per year . The exemplary  90 kW   PV system,integratedover the entire surface andoriented  north-south ,generates 78,900  kWh/a. With this,  the church hasanenergy supply  of

221% .

221%  PEB churchrenovation, 8123 Ebmatingen/ZH

The Roman Catholic Church of St. Francis Ebmatingen , built in  1989, urgently neededtoberenovated . An old oil-fired heatingsystem, an  outdated   insulation system and a leaking roof in placesresulted in a disproportionately high  energy requirementof 84,400  kWh/a. In the winter of 2018/19 ,the building and energy  renovation followed with  new insulation, a geothermal probe heat pump,  photovoltaic with   thermal energy(PVT) and LED lighting. As a result of these measures ,the previous total energy requirement  of 84,400  kWh/a  fell by

35% to 54,700 kWh/a. The character of the

The PlusEnergy Church was nevertheless preserved.

The refurbishment costs amount  to CHF 1.2 million. Of the total of 543 m2  of the  PV system, whichis optimally integratedinto the roof , 161  m2  areequippedwith PVT modules .In addition to  electricity ,theyalso produce 41,800  kWh/a of  heat, which  in summerisfed  300 m deep into the ground . In winter , part of itis  recovered again.

The installed capacity of the PV/PVT system is 90 kW. This means that  annually

78,900  kWh/a  CO2-free electricity and   41,800 kWh/a thermal energy generated by the 161  m2 ofthermal solar collectors .

Both plants generatea total of 120,700 kWh/a. This means that  the  PEB churchhasan energy supply  of 221% .

Therenovation of the church  servesas a model  both intermsof  energy and   ecology .  The PEB church of St. Franziskus Ebmatingen willreceivethePlusEnergieBau Solar Prize  2019for this .

The CatholicChurch of St. Francis in Ebmatingen  (ZH),built in 1989, was indire  needof   renovation. With an old  oil heating system  ,  inadequate  insulationand a roof that leaked in places, it required adisproportionately  high  energy  demand of  84,400 kWh/a. Inthe winter of 2018/19, thestructural and energy  renovation  included   new insulation, a geothermal  heat pump , aphotovoltaic and thermal (PV-T)   infrastructure  and LED lighting. These measures  reduced  consumptionby 35% ,  from 84,400 to 54,700 kWh/a.

Theoriginal appearanceof  theBEPchurchhas  been  preservedandthe   renovation cost 1.2  million  francs. Of the 543  m2 ofthe roof-integrated     PV system,161 m2 are  equippedwithPV-T  modules.  They produce electricity  but also 41'800 kWh/aof  additional heat . Theheat isinjected into the ground ata depth of  300 m inthe summerand  recovered inthe winter bymeans of  a heat pump .

Withan outputof   90  kWp,  thePV-Tsub-structure    generates 78,900 kWh/a  CO2-free  . The BEPchurch supplies a total of

120'700 kWh/a andthus  ensures a self-provisioning

duction de 221%.

Theentire  renovation is a great  success story  from  energy and ecological point of view . The CatholicChurch of  St.Francis  Ebmatingen awarded the BEP 2019Solar Prize for this .

Technical data

Thermal Insulation

| Roof: floor: windows: | 24 cm 8 cm triple | U-value: U-value: U-value: | 0.16 W/m2K 0.19 W/m2K 0.70 W/m2K |  |
| --- | --- | --- | --- | --- |
| Energy demand before renovation [100%[ 154%]. |  |  |  |  |
| EBF: 1'070 m2 |  | kWh/m2a | % | kWh/a |
| Hot water: |  | 4.3 | 6 | 4’601 |
| heating: |  | 68 | 86 | 72’760 |
| Electricity: |  | 6.6 | 8 | 7’062 |
| Total EB: |  | 78.9 | 100 | 84’423 |

wall:	9 cm	U-value:	0.21 W/m2K

Energy demand after  [65%|   100%]

EBF: 1'070 m2	kWh/m2a	% 	kWh/a

Hot water:	1.0 	2 	1’075

Solar :	39.0 	77 	41’766

Electricity WP:	6.4 	12 	6’813

Electricity: 	4.7 	9 	5’029

Total EB:	51.1      	54’683

Energy supply

Own-EV:	m2         kWp  kWh/m2a	% 	kWh/a

PV:	543     89.9 	145.2 144.2 	78’881

| SK roof: 161 259.5 Own energy supply | 76.4 221 | 41’776 120’657 |
| --- | --- | --- |
| Energy balance (final energy) | % | kWh/a |
| Own energy supply | 221 | 120’657 |
| total energy demand: | 100 | 57’683 |
| Solar power surplus: | 120 | 62’974 |

Confirmed by the cantonal electricity companies

Zurich (EKZ) on 08.07.2019

Daniel Meier, phone +41 58 359 57 40

Personsinvolved

Location of the building

Roman CatholicChurch St. Francis

Parish vicariate Maur

Bachtelstrasse 13, 8123 Ebmatingen/ZH Tel. 044 980 19 90, pastoral. eb@zh.kath.ch

Client

Roman Catholic parish Egg/ZH President of , Louis Landolt Flurstrasse 10, 8132 Egg/ZH

Architect

Studer Architect

D. Studer, dipl. Arch. ETH SIA Hüttenmattweg 19, 5213 Villnachern

41 79 324 17 00, d.studer@studerarchitekt.ch

HLS planner

W+P   AG, Marlon Keller

Zweierstr. 129, 8003 Zurich

41 44 454 10 64, m.keller@wpe.ch

PVT planner

BS2 AG, Dr. Niklaus Haller, Brandstr. 33, 8952 Schlie- ren, Tel. +41 44 275 25 09, haller@bs2.ch

Realisation of PV systems

winsun AG, Benjamin Wenger, Rheinweg 1, 8200

Schaffhausen, Tel. +41 52 212 27 00, info@winsun.ch

42|          SwissSolar Prize  2019|          Prix Solaire Suisse 2019

1

2 	3

1  The optimally integrated  PV roof systemof thePlusEnergie-Kirche  generates78,881  kWh ofCO2-free solar power annually .

2  Before the refurbishment ,theenergy requirement was

84'400 kWh/a.

3  The fully integrated  PVT roof systemproduces 41,800 kWh/a of thermal energy inaddition  to electricity .

Swiss Solar Prize 2019|          Prix Solaire Suisse 2019|       43